No.2798/T2/20/KSFDC 					                       12.01.2022

Tender Cost ---- Rs 681/- (Inc GST)

SUBJECT:COMPREHENSIVE ANNUAL MAINTENANCE & SERVICE CONTRACT FOR PACKAGE & Split  AIR-CONDITIONERS.

Dear Sir,

Sealed Tenders are invited from original equipment manufacturers and their authorized dealers of air conditioners to reach on or before 3:00 PM, 19.01.2022, along with an EMD of Rs.4331/- in the form of D.D. in favour of The Managing Director , KERALA STATE FILM DEVELOPMENT CORPORATION LTD, Chalachithra Kalabhavan   Trivandrum. for the work of “ANNUAL MAINTENANCE & SERVICE CONTRACT FOR PACKAGE & SPLIT AIR-CONDITIONERS @ Kairali/Sree/Nila Thampanoor Trivandrum and Kalabhavan Theatre Vazhuthacaud, Trivandrum” as per terms and conditions and schedule enclosed herewith.

(Tentative CAMC period: 20.01.2022 to 19.01.2023)

Tenders without seal or EMD will be summarily rejected.

Yours faithfully,

MANAGING DIRECTOR

The Managing Director KSFDC invites Tender from the following.

Eligibility Criteria (documents may be enclosed in the following order)

- OEM or their authorized dealers having turnover of not less than One crore every year in the previous three financial years including year (2019 – 2020), (Please submit Annual Report (Balance Sheet and Profit & Loss Account) for the last three financial years)

- Bidder must have previous experience of successfully executing at least 03 (three) works of Annual Maintenance Contract [CAMC] for Air conditioning systems during the last three (03) years (as on date 31.12.2021) in multiple locations in the state of Kerala to Government Institutions/ undertakings/ affiliated bodies/recognized educational institutions, Banks/financial institutions/PSUs either directly or through nationally reputed OEMs and System Integrators. The Bidder must submit documentary evidence of supply orders/copy of agreement/work completion/satisfactory letters that substantiate fulfillment of the above criteria and information. Three similar orders each costing not less than Rs. 100,000/- (Similar works means Providing CAMC for Air conditioners (minimum 17 / 22 Tonnage).

- The Bidder should be registered for GST and PAN no (Submit copy of Registration Certificate and PAN Card)

- The Bidder should be manufacturer or authorized sales and service provider of any ISO certified Air Conditioning system ( Submit copy of Authorization with validity )

- Tenders without signature, seal on all pages & EMD will be summarily rejected.

Tender Fee and EMD exempted for MSME ( Micro Small & Medium Enterprises ) and NSIC Units Subject to submission of valid MSME and NSIC certificate.

Scope of Work: The tender is for the Comprehensive Annual Maintenance Contract of Package and Split Air conditioners

The cover shall be super scribed “Tender for CAMC of AC units at Kairali/Sree/Nila & Kalabhavan Theatre, KSFDC Ltd., Thiruvananthapuram”.

Sealed Tenders received will be opened at 3:30 PM on 19.01.2022 in the presence of available bidders or their representatives.

Managing Director, KSFDC will have the right to accept or reject any or all quotations without assigning any reason what so ever.

The EMDs of the first three lowest bidders will be retained till finalization.  The EMDs of others will be released after tender evaluation.

CONTRACTOR                                                                                                   MANAGING DIRECTOR

## TERMS AND CONDITIONS

# MAINTENANCE AND SERVICE CONTRACT FOR PACKAGE & SPLIT AIR-CONDITIONERS.

- All the machines will be in working condition at the time of commencement of contract. The contractor will have to hand over all the machines in working condition at the time of completion of contract. Payments will be released only if all the  machines are in working condition as recommended by the unit head/technician KSFDC.

- All the machines should be inspected once in every month. (Pressure pump service once in 3 months).

- This contract includes repair and replacement of all controls, PC Boards, compressors, fan motors including gas charging excluding sheet metal work. The compressor and other spares  which are in original condition will have to be replaced with new compressors of same make and specification when they fail, the cut compressors can be got repaired. The refrigerant shall be eco-friendly gasses like HFC or latest, These eco friendly refrigerants shall be with  zero Ozone depleting substances ( R32 & R410 A )

- The contractor has to deploy enough technicians and helpers for the servicing and attending breakdown of machines.

- On acceptance of the rates quoted by the contractor, the contractor will be allowed to start the work only after producing the receipt of the security deposit @ 3% of the cost of maintenance and service contract. 3% of the total order value will be submitted as security deposit till the expiry of defect liability period of one year.

- The Tenderer shall be amenable to techno commercial discussions & negotiations.

- The successful Tenderer may execute an agreement on stamp paper worth Rs.200/- before commencing CAMC period.

- If the Contractor fails to honor the work order EMD will be forfeited.

- The payment will be made quarterly only after satisfactory completion of three monthly services on production of GST invoice. EMD & security deposit will be released after releasing final bill amount on production of original receipts.

- The contract may be renewed for another year on same terms & conditions if performance is found to be satisfactory.

- If the contractor shall make default in any one or more of the following respects that is to say :

  - If the contractor without reasonable cause wholly suspends the carrying out of work before completion thereof or

  - If the contractor fails to proceed regularly or diligently with the work or

  - If the contractor refuses or persistently neglects to comply with the written notice from KSFDC asking him to remove defective work or improper material or goods, the Managing Director KSFDC, has the right to terminate the contract immediately.

- If a complaint is not rectified from the date of booking of the complaint, penalty of Rs. 500/- per day will be levied by the unit head until the complaint is rectified.

Managing Director KSFDC will be the sole authority to take the decision.

CONTRACTOR                                                                                                   MANAGING DIRECTOR

CAMC SCOPE OF SERVICES

The brief scope of services and obligations to be performed by the contractor not withstanding to those mentioned in the periodic maintenance checklist/maintenance plan are the following.

- Quarterly checking and servicing the entire plant (Quarterly preventive maintenance)

- Attending to the plant when called upon by the client within one hour.

- Repairing/overhauling the components of the equipment at site/in service station, including replacement of worn out parts when found necessary.

- Replenishing refrigerant required as a result of leak in the system arising out of wear and tear

- Lubricating the bearings of motor, pumps and fans, when found necessary.

- Replacing of damaged electrical parts before restarting the system after break down.

- Quarterly inspecting belts, adjusting of tension and replacing worn out belts.

- Painting of equipment covered under this scheme once in one years.

- Check control system and devices for evidence of improper operation. Repair, adjust or replace components to ensure proper operation.

- Check for proper operation of cooling coil. Clean, restore or replace as required.

- Check motor contactor for pitting or other signs of damage. Repair or replace as needed.

- Check fan blades. Clean, repair or replace as needed.

- Check refrigerant system temperatures. If outside recommended levels, find cause, repair and adjust refrigerant to achieve optimal operating levels.

- Check integrity of all panels on equipment. Replace fasteners as needed to ensure proper integrity and fit finish of equipment.

- Check drain pan, drain line and coil for biological growth. Clean as needed.

- Visually inspect areas of moisture accumulation for biological growth. If present, clean or disinfect as needed.

- Check compressor oil level and or pressure on refrigerant systems having oil level and or pressure measurement means. Repair, replace or adjust as needed to ensure proper control

- Check for proper damper operation. Repair or replace as needed.

- Check temperature transmitters for accuracy.

- Visually inspect exposed duct work and external piping for insulation and vapor barrier for integrity. Correct as needed.

- Visually inspect internally lined duct work until the first turn or up to 20 ft into the supply plenum from air system for integrity, and if soiled or degraded, correct. Records are to be maintained for all the above tasks and submitted to client as and when required.

- Inspecting the PAC and carrying out preventive maintenance as per the standard practice quarterly.

- Checking the refrigeration system, motor and starters and ensuring healthy condition of the plant.

- Checking the system for any leaks and rectification of leaks if found.

- Taking set of readings and evaluating to ensure satisfactory performance of the plant.

- Checking the Refrigeration control system for operation and adjusting the settings.

- Cleaning Air Cooled condenser once in a year, if found necessary.

CONTRACTOR                                                                    MANAGING DIRECTOR

- Cleaning the evaporator once in a years, if found necessary.

- Checking the functioning of compressor and its accessories.

- Lubricating the bearings of motors & fans when found necessary.

- Quarterly inspection of belts, adjusting the tension and replacing the worn out belts as and when found required.

- Overhauling / repairing the components of the equipment at site or in service station as and when required including providing loan compressor for scroll units in case of failure of the compressor.

- Replenishment of Refrigerant gas as a result of leak developed due to wear & tear.

- Annual checking of compressor oil and changing if found necessary.

- Checking of the microprocessor controller for its proper functioning and repair / replacement of the same if found necessary.

- Attending to complaint / breakdown calls whenever called upon / required (Max twelve times a year) during normal working hours.

- Reporting the healthiness of the plant and suggesting improvements if any.

- Replacement of compressor, condenser coil, evaporator coil, condenser etc as and when required.

NOT COVERED UNDER THE COMPREHENSIVE ANNUAL MAINTENANCE SERVICE

- Day to day operations, routine maintenance and house keeping.

- Replacement of sheet metal panels etc that has undergone deterioration due to atmospheric conditions / experimental factor ageing etc.

- Repairing / replacement of ducting and its accessories like dampers of all types, thermal and acoustic insulation, all types of piping’s and valves, electrical panels, cables, control wirings, bulbs, fuses etc.

- Any replenishment of consumable and failures of equipments pertaining to equipment capacity mismatch between high and low side.

- Pneumatic controls, pressure gauges and thermometers.

- Replacement of imported controls, pressure switches, gauges, modulating valves, modulating motors, microprocessor & BMS components.

- Any welding work connected to above.

- All kind of civil and structural works.

- Any other items not specifically included by us.

The Maintenance Service is subject to termination by the Contractor if repairs/overhauls are carried out by third party without the written approval of the Contractor.

The Maintenance Service can be terminated by either party in which case a pro-rata refund of the fee will be made by the Contractor for the unexpired full quarterly period.

The scheme does not cover damage to equipment / ancillaries or failure due to environmental conditions, due to any fluctuations of Voltage beyond 415V +/-5%

Consequential / collateral damages and production losses of any nature what so ever are not covered under this scheme.

CONTRACTOR                                                                                                   MANAGING DIRECTOR

The Contractor shall not be liable for any breach or non-performance or delay in carrying out any of the obligations contained in the Maintenance Service leaflet enclosed as a result of strike, lockout, industrial/labour disturbance, fire/accidental damage, restrictions imposed by Government, any act of God, riots, war or any condition arising from similar causes beyond their control.

Power and water supply for repair work has to be provided by customer, free of cost.

CONTRACTOR                                                                    MANAGING DIRECTOR